## Sheet1
Building size | Length | Area_perimtr_wall | Area_core_wall | Plan Area Perimeter | Plan Area Core | Specific Heat*Density |  |  | Conductivity |  | Window Conductivity | Window Ratio | C_e |  | C_p |  | C_i |  | C_c |  | R1 |  | R2 |  | R3 |  | R4 |  | R_win
[6 empty] | Air | Minimum | Maximum | Minimum | Maximum |  |  | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum
ft | ft | ft^2 | ft^2 | ft^2 | ft^2 | Btu/ft^3*F | Btu/ft^3*F | Btu/ft^3*F | Btu/hr*ft*F | Btu/hr*ft*F | Btu/hr*ft^2*F |  | Btu/F | Btu/F | Btu/F | Btu/F | Btu/F | Btu/F | Btu/F | Btu/F | hr*F/Btu | hr*F/Btu | hr*F/Btu | hr*F/Btu | hr*F/Btu | hr*F/Btu | hr*F/Btu | hr*F/Btu | hr*F/Btu
60 | 2 | 2400 | 1200 | 2700 | 900 | 0.019323 | 0.638 | 30.18 | 0.017 | 0.808 | 0.5 | 0.5 | 1531.2 | 72432 | 521.7313 | 17226 | 765.6 | 36216 | 173.9104 | 5742 | 0.0010314 | 0.04902 | 0.0010314 | 0.04902 | 0.0020627 | 0.098039 | 0.0020627 | 0.098039 | 0.0016667
80 | 2 | 3200 | 2000 | 3900 | 2500 | 0.019323 | 0.638 | 30.18 | 0.017 | 0.808 | 0.5 | 0.5 | 2041.6 | 96576 | 753.6118 | 24882 | 1276 | 60360 | 483.0845 | 15950 | 0.00077351 | 0.036765 | 0.00077351 | 0.036765 | 0.0012376 | 0.058824 | 0.0012376 | 0.058824 | 0.00125
100 | 2 | 4000 | 2800 | 5100 | 4900 | 0.019323 | 0.638 | 30.18 | 0.017 | 0.808 | 0.5 | 0.5 | 2552 | 120720 | 985.4924 | 32538 | 1786.4 | 84504 | 946.8456 | 31262 | 0.00061881 | 0.029412 | 0.00061881 | 0.029412 | 0.00088402 | 0.042017 | 0.00088402 | 0.042017 | 0.001
150 | 2 | 6000 | 4800 | 8100 | 14400 | 0.019323 | 0.638 | 30.18 | 0.017 | 0.808 | 0.5 | 0.5 | 3828 | 181080 | 1565.1938 | 51678 | 3062.4 | 144864 | 2782.5667 | 91872 | 0.00041254 | 0.019608 | 0.00041254 | 0.019608 | 0.00051568 | 0.02451 | 0.00051568 | 0.02451 | 0.00066667
200 | 2 | 8000 | 6800 | 11100 | 28900 | 0.019323 | 0.638 | 30.18 | 0.017 | 0.808 | 0.5 | 0.5 | 5104 | 241440 | 2144.8952 | 70818 | 4338.4 | 205224 | 5584.4568 | 184382 | 0.00030941 | 0.014706 | 0.00030941 | 0.014706 | 0.00036401 | 0.017301 | 0.00036401 | 0.017301 | 0.0005
[13 empty] | C_e |  | C_p |  | C_i |  | C_c |  | R1 |  | R2 |  | R3 |  | R4 |  | R_win
[7 empty] | Note: C = rho*specific_heat*L*A; R= L/conductivity*A | [5 empty] | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum
[13 empty] | KiloJoules/Celcius | KJ/C | KJ/C | KJ/C | KJ/C | KJ/C | KJ/C | KJ/C | Celcius/Watt | C/W | C/W | C/W | C/W | C/W | C/W | C/W | C/W
[9 empty] | in SI units ----> |  |  |  | 2909.28 | 137620.8 | 991.2894 | 32729.4 | 1454.64 | 68810.4 | 330.4298 | 10909.8 | 0.0019554 | 0.092941 | 0.0019554 | 0.092941 | 0.0039109 | 0.18588 | 0.0039109 | 0.18588 | 0.00316
[13 empty] | 3879.04 | 183494.4 | 1431.8625 | 47275.8 | 2424.4 | 114684 | 917.8605 | 30305 | 0.0014666 | 0.069706 | 0.0014666 | 0.069706 | 0.0023465 | 0.11153 | 0.0023465 | 0.11153 | 0.00237
[13 empty] | 4848.8 | 229368 | 1872.4355 | 61822.2 | 3394.16 | 160557.6 | 1799.0067 | 59397.8 | 0.0011733 | 0.055765 | 0.0011733 | 0.055765 | 0.0016761 | 0.079664 | 0.0016761 | 0.079664 | 0.001896
[13 empty] | 7273.2 | 344052 | 2973.8682 | 98188.2 | 5818.56 | 275241.6 | 5286.8768 | 174556.8 | 0.00078218 | 0.037176 | 0.00078218 | 0.037176 | 0.00097772 | 0.046471 | 0.00097772 | 0.046471 | 0.001264
[13 empty] | 9697.6 | 458736 | 4075.3008 | 134554.2 | 8242.96 | 389925.6 | 10610.468 | 350325.8 | 0.00058663 | 0.027882 | 0.00058663 | 0.027882 | 0.00069016 | 0.032803 | 0.00069016 | 0.032803 | 0.000948
[12 empty] | Most probable values to be used as a starting point | C_e | C_p | C_i | C_c | R1 | R2 | R3 | R4
[10 empty] | U value | Watts/m2/K |  | KJ/C | KJ/C | KJ/C | KJ/C | K/W | K/W | K/W | K/W
[10 empty] | 0.09 | 0.01585 |  | 8727.84 | 2973.8682 | 4363.92 | 991.2894 | 0.026288 | 0.026288 | 0.026288 | 0.026288
[10 empty] | 0.09 | 0.01585 |  | 11637.12 | 4295.5874 | 7273.2 | 2753.5817 | 0.019716 | 0.019716 | 0.015773 | 0.015773
[10 empty] | 0.09 | 0.01585 |  | 14546.4 | 5617.3066 | 10182.48 | 5397.02 | 0.015773 | 0.015773 | 0.011266 | 0.011266
[10 empty] | 0.09 | 0.01585 |  | 21819.6 | 8921.6045 | 17455.68 | 15860.6303 | 0.010515 | 0.010515 | 0.0065721 | 0.0065721
[10 empty] | 0.09 | 0.01585 |  | 29092.8 | 12225.9025 | 24728.88 | 31831.4039 | 0.0078865 | 0.0078865 | 0.0046391 | 0.0046391